# 5313F	FORMAN CONCEALED SUSPENDED CEILING SYSTEMS

## 1.	GENERAL

This section relates to the supply and installation of Forman Building Systems suspended sheet or flush ceiling systems, comprising of:

-	Rondo furring channel system, supporting screw fixed sheet materials,

-	all elements offered by the manufacturer to complete the system.

### 1.1	RELATED SECTIONS

Refer to 5113G GIB® PLASTERBOARD LININGS for stopping of plasterboard sheets

### 1.2	ABBREVIATIONS

The following abbreviations are used throughout this part of the specification:

FRR	Fire resistance rating

NRC	Noise reduction coefficient

CAC	Ceiling attenuation class

Documents

### 1.3	DOCUMENTS

Documents referred to in this section are:

NZBC C/AS1	Fire safety

AS/NZS 1170.1	Structural design actions - Permanent, imposed and other actions

NZS 1170.5	Structural design actions - Earthquake actions - New Zealand

AS/NZS 2588	Gypsum plasterboard

AS/NZS 2785	Suspended ceilings - Design and installation

NZS 4219	Seismic performance of engineering systems in buildings

AS 2946	Suspended ceilings, recessed luminaires and air diffusers - Interface requirements for physical compatibility

ASTM E1414	Standard test method for airborne sound attenuation between rooms sharing a common ceiling plenum (two room method)

Documents listed above and cited in the clauses that follow are part of this specification.  However, this specification takes precedence in the event of it being at variance with the cited document.

### 1.4	MANUFACTURER'S DOCUMENTS

Manufacturer's and supplier's documents relating to work in this section are:

Rondo:	Concealed Suspended Ceiling Systems

Access Panels Slimline and Panther

Nittobo:	Solaton T&G staple and adhesive

Parafon:	Ceiling tile range direct fix.

Novahush:	Baffle Stack Inter-office Sound Control Systems

Firefly;	Fire and smoke Barriers, and accessories

BRANZ Opinion FAR 1627 Firefly Canopies in Fire Resistance Floor Systems

BRANZ Opinion FAR 2701 Resistance of Firefly Phoenix Cavity Fire Barrier

BRANZ Opinion FAR 1628 Fire Resistance of Firefly Plus 60 Cavity Fire Barrier

Manufacturer/supplier contact details

Company:	Forman Building Systems Ltd

Web:	www.forman.co.nz/products.php

Telephone:	0800 45 4000

Requirements

### 1.5	NO SUBSTITUTIONS

Substitutions are not permitted to any specified system, or associated components and products.

### 1.6	SAMPLE SECTION

Allow to erect a sample section of the suspended ceiling system offered.  Subject to confirmation in writing, the sample section may form part of the completed installation.

Refer to SELECTIONS for location of sample section.

### 1.7	INSTALLATION

To AS/NZS 2785.  Installation by a manufacturer's accredited installer, using the manufacturer's technical services.  Provide evidence of experience, listing completed projects of similar size and complexity.  Installation of Firefly Cavity Barriers must be by trained installers.

Installation to comply with the loadings code AS/NZS 1170.1.  Installation to comply with the requirements of NZS 4219; with related building services installations complying specifically with clauses 5.9 Ducting, 5.14 Luminaires, and 5.13 Ceiling-suspended equipment and equipment in ceiling voids.

### 1.8	CLEANING INSTRUCTIONS

Supply information on the materials and method of cleaning the ceiling system over its expected life.

### 1.9	SPARES

Provide spare matching ceiling elements in the quantities specified in SELECTIONS.  Deliver into a dry store at the site or elsewhere as directed and at agreed times.

Performance

### 1.10	LOADING CODE REQUIREMENT

Comply with the requirements of AS/NZS 1170.1 or NZS 1170.5.

### 1.11	CERTIFICATION

Provide:

-	certification of compliance with NZS 1170.5, section 8 for evaluation

-	certificates and other evidence that the system offered complies with the standards of performance specified

-	a Producer Statement on completion.

### 1.12	ACOUSTIC REQUIREMENTS

Refer to SELECTIONS for requirements.  Use an independent testing authority to test a specimen of the ceiling system to ASTM E1414, and submit the results for acceptance.

### 1.13	EARLY FIRE HAZARD PROPERTIES

Early fire hazard properties of the finished internal surface materials/systems when tested to NZBC C/AS1, Appendix C, Test Methods, must not exceed the following indices to NZBC C/AS1, Table 6.2.

| Properties | Index | Item | Location |
| --- | --- | --- | --- |
| (FI) Flammability index | ~ | Suspended fabrics | ~ |
| (SFI) Spread of flame index | 0 | Ceilings | Exitways |
| (SFI) Spread of flame index | ~ | ~ | ~ |
| (SDI) Smoke development index | 3 | Ceilings | Exitways |
| (SDI) Smoke development index | ~ | ~ | ~ |

### 1.14	FIRE RATING REQUIREMENT

Design the ceiling system, including cavity fire and smoke barriers where required, so that together with the floor it is to NZBC C/AS1: Part 5 Fire resistance ratings.  Refer to SELECTIONS for requirements.

### 1.15	ENVIRONMENTAL REQUIREMENTS

Design the ceiling system for use over its expected life without deterioration.  Refer to SELECTIONS for requirements.

### 1.16	REFLECTANCE

Refer to SELECTIONS for requirements.

## 2.	PRODUCTS

Materials - Rondo Key-Lock suspended flush ceilings

### 2.1	GRID SUSPENSION SYSTEM

System:	Rondo Key-Lock building board suspension system

Supplied by Forman Building Systems

Freephone: 0800 45 4000.

### 2.2	GRID DIRECT FIX SYSTEM

System:	Rondo Key-Lock building board suspension system

Supplied by Forman Building Systems

Freephone: 0800 45 4000.

Hot-dip galvanized steel elements to AS/NZS 2785, including furring channels and direct fix brackets for fixing to timber, steel and concrete.

### 2.3	PLASTERBOARD SHEET

GIB® plasterboard to AS/NZS 2588.

### 2.4	CSR GYPROC® PERFORATED PLASTERBOARD

Gyproc® perforated plasterboard ceiling system.

### 2.5	BORAL ECHOSTOP® PERFORATED PLASTERBOARD

Boral Echostop® perforated plasterboard ceiling system, with 12mm square holes.

### 2.6	ACCESS PANELS

Refer to SELECTIONS for product selections.

Materials - above ceiling acoustic baffles (non-fire rated)

### 2.7	ABOVE CEILING ACOUSTIC BAFFLES

System:	Forman Baffle Stack inter-office sound control system

Materials - above ceiling cavity fire barriers

### 2.8	ABOVE CEILING CAVITY FIRE BARRIERS

System:	Forman Firefly cavity fire barriers made from non-respirable glass textile, fire tested with full penetration systems

-/60/60	Forman Firefly Titan fire rated cavity barrier fixed with Rondo steel stud and Keylock wall angle, in accordance with the manufacturer's instructions.

-/60/38	Forman Firefly Plus 60 fire rated cavity barrier fixed with Rondo steel stud and Keylock wall angle, in accordance with the manufacturer's instructions.  Maximum drop 6.1 metres

-/60/30	Forman Firefly Plus 30 fire rated cavity barrier fixed with Rondo steel stud and Keylock wall angle, in accordance with the manufacturer's instructions.  Maximum drop 6.1 metres

-/90/-	Forman Firefly Phoenix smoke and fire barrier fixed with Rondo steel stud and Keylock wall angle, in accordance with the manufacturer's instructions.  Maximum drop 6.1 metres

Firefly cavity smoke, flame and fire barriers must be installed by trained installers using proprietary Firefly Collars, Firefly Shield and Firefly Adhesive.

Components

### 2.9	FASTENERS SUSPENSION SYSTEM

Join furring channels and C channels using pop rivets or 8g-16 x 12mm (minimum) self drilling wafer head screws.

### 2.10	FASTENERS DIRECT FIX

8g-16 x 25mm (minimum) self drilling wafer head screws or 30mm clouts for fixing to timber.

### 2.11	SCREWS

25mm x 6 gauge non-rusting Type S self-drilling and self-tapping buglehead screws.

## 3.	EXECUTION

Conditions

### 3.1	CO-ORDINATE SERVICES

Co-ordinate and co-operate with electrical and mechanical work to avoid conflict between suspension members and luminaires, diffusers, pipework and ducting.  Confirm the provision of extra hangers and fixings.

Ensure co-operation with work in and above the ceiling, including the marking of specific ceiling tiles below major access points to above-ceiling services.  Colour coded markings to follow the standards laid down by mechanical and electrical services.

### 3.2	SITE CONDITIONS

Do not begin installation until the building is closed in, fully glazed, the roof watertight, and mechanical and electrical duct work above the ceiling completed.

### 3.3	COMPLY

Comply with AS 2946 for interface requirements for physical compatibility.

### 3.4	RESPONSIBILITY

Ensure that conditions are suitable for the ceiling installation.  Arrange for the programming of the work to suit required practice.

Application

### 3.5	INSTALL

Install the system to AS/NZS 2785 minimum standards and the ceiling manufacturer's requirements.

### 3.6	INSTALL ABOVE CEILING ACOUSTIC BAFFLES

Install Baffle Stack with enough compression to ensure stability between slab, roof, or floor above.  No gaps allowed through the width of the baffle.

### 3.7	INSTALL ABOVE CEILING CAVITY FIRE BARRIERS

Install Firefly Cavity Fire Barriers in accordance with the manufacturer's installation manual and BRANZ opinions.

### 3.8	ACCESSIBILITY

Provide access to the ceiling system and the in-ceiling and above-ceiling services so that maintenance and removal of any part can be carried out without damage to the ceiling system or panels.

### 3.9	PENETRATIONS

Accommodate recessed light fittings, air conditioning outlets and other electrical and/or mechanical services that are fixed to or pass through the ceiling system.  Provide independent support for these as necessary.

### 3.10	RETURN AIR PLENUM

Use materials that do not release fibres into the ceiling space, air conditioning or ventilation system.

### 3.11	FLUSH CEILING

Install the Forman Rondo Keylock suspension system to AS/NZS 2785 minimum standards.  Screw-fix sheets to furring channel sections at the centres required by the ceiling lining manufacturer.  Stagger joints and fully support on sections, with strongbacks at centres to suit the load and Rondo installation manual.  Refer to 5113G GIB® PLASTERBOARD LININGS for plasterboard stopping specification.

### 3.12	PROTECT EXISTING WORK

Protect adjacent existing work from damage during the installation.

Completion

### 3.13	REPLACE

Replace damaged or marked elements.

### 3.14	LEAVE

Leave work to the standard required by following procedures.

### 3.15	REMOVE

Remove debris, unused elements and elements from the site.

### 3.16	CLEAN

Clean soiled or marked units.

## 4.	SELECTIONS

For further details on selections go to www.forman.co.nz/products.php

Substitutions are not permitted to the following, unless stated otherwise.

### 4.1	SAMPLE SECTION

Location:	~

### 4.2	SPARES

Spares:	~

### 4.3	PERFORMANCE REQUIREMENTS

Acoustic

NRC:	~ minimum

Attenuation Class:	~ minimum room to room

Fire

Location:	~

FRR:	~ minimum

Cavity barrier:	~

Floor system:	~

Environmental

Range:	~ - ~°C

Relative humidity:	~ % maximum

Light reflectance

Reflectance:	~ % minimum

For (colour):	~

Recycled content

Percentage:	~ % minimum

Grid and tile system

### 4.4	FLUSH CEILING SUSPENSION SYSTEM

Rondo Key-Lock building board suspension system from Forman Building Systems.

Location:	~

Ceiling lining:	~

FRR:	~

### 4.5	CEILING TILES

Brand:	~

Type:	~

Pattern:	~

Thickness:	~mm

Size:	~mm x ~mm to suit grid

Edge profile:	T&G

### 4.6	PERFORATED PLASTERBOARD SHEET

Brand:	~

Thickness:	13mm

Insulation:	~mm

### 4.7	ACCESS PANELS

Rondo Panther access panels.

FRR:	~

Acoustic rating:	~

Finish/colour:	~

Size:	~mm x ~mm

Edge:	Standard

Lock:	Budget lock